Integrating the PV-Diesel Hybrid System for Reliability Improvement in Distribution System
Cho Cho Myint 
Department of Electrical Power Engineering
Yangon Technological University
Yangon, Myanmar
aecho862015@gmail.com

Ohn Zin Lin 
Department of Electrical Power Engineering
Yangon Technological University
Yangon, Myanmar
ohnzinlin@ytu.edu.mm

Soe Soe Ei Aung 
Department of Electrical Power Engineering
Yangon Technological University
Yangon, Myanmar
soesoeeiaung80@gmail.com




Abstract— In Myanmar, as the main power generation is hydro power generation. the utility cannot supply sufficient power to customers during the dry season. Besides interruptions occur frequently due to aging system and lack of prospered protection. Therefore, reliability is an urgent issue in Myanmar. As a result of unbalance between generation and load, the distribution system is getting poor voltage profile, instability and high power losses in high load condition. According to network characteristics, the failure of a component always leads to consequence interruption in a radial distribution system.  Therefore, it is a must consideration to mitigate these challenges to enhance the system reliability. There are many techniques to solve the reliability problems such as reclosers, switching devices (manual and automated switches), system reconfiguration, feeder re-conducting and integration of distributed generation (DG). In this paper, system reliability assessment is evaluated in detail with the integration of the distributed generation such as PV-Diesel Hybrid System. The location of DG is chosen according to the expected energy not supply (EENS) and the voltage drop in proposed system. Next, the optimal sizing of DG is chosen depends on the penetration level of generator. Reliability indices can be evaluated depending on the failure rate(λ), repair time(r) and annual outage time(U) in Electrical Transient and Analysis Program (ETAP) software. The case study of this thesis is carried out in 33/11 kV network which is connected Kyatminton Substation, Kyaukse, Middle Myanmar. 
Keywords— distribution system, reliability, reliability indices, EENS, distributed generation,
I. Introduction 
Electrical distribution systems are essential part of the electrical power system. In distribution network, flow of power is unidirectional and consumer at the far end getting low voltage as compare to consumer close to substation. There are two basic types of distribution system: meshed and radial systems [6]. A mesh system has multiple sources of supply operating in parallel. Therefore, Evaluation methods for meshed distribution systems are conceptually the same as those used for composite systems. A radial system is arranged like a tree where each customer has one source of supply. Therefore, the techniques for a radial distribution system are based on failure-mode analysis including considerations of all realistic failure and restoration processes [7].


The reliability concepts of distribution system differ from generation and transmission systems. Generation and transmission reliability mainly emphasizes capacity and loss of load probability, configuration whereas the distribution reliability looks like the engineering design, planning and operations. It is important to note that the distribution system is a vital link between the bulk power system and its customers. In many cases, these links are radial in nature that makes them vulnerable to customer interruptions due to a single outage event. A radial distribution circuit generally uses main feeders and lateral distributors to supply customer energy requirements. The distribution system occurs the failures that have 90% of all customer interruption according to the reported in literature [8]. 


In this thesis, distribution system reliability is mainly analyzed in Kyaukse Feeder line in Kyatminton (Kyaukse) Substation, Kyaukse in Mandalay Division as case study because the Kyaukse area is situated in Mandalay region (dry zone area) and then it has more interruption than others feeder line according to the collected data. The source of power supply to Kyaukse Substation is fed from Belin Station which is obtain the main supply from Yeywa and Shweli hydro power station.  When it has been coming in dry season, the system always has to be Load-Shed when the Yeywa dam has insufficient water to drive the water turbine.Therefore, system reliability is required to improve in Kyaukse area. 


There are many techniques to solve the reliability problems such as reclosers, switching devices (manual and automated switches), system reconfiguration, feeder re-conducting and integration of distributed generation (DG) [9]. Distributed generation (DG) is one of the solutions to improve the system reliability. DG is often used as backup power to enhance reliability or as a means of deferring investment in transmission and distribution network, avoiding network charges, reducing line losses, deferring construction of large generation facilities, displacing expensive grid-power supply, providing environmental benefits [11], [14].
II. Background Theory of Reliability
Reliability is the probability of success or the probability that the system will perform its intended function under specified design limits [1]. Power system reliability assessment can be divided into the two basic aspects of system adequacy and system security. Adequacy is associated with static conditions which do not include system dynamic and transient disturbances. Security is associated with the response of the system to whatever perturbations it is subject to [2].

Distribution system of this paper based on analytical evaluation involves assessment of suitable adequacy indices at the actual consumer load points. The basic load point indices are the load point failure rate (λ), the average outage time (r) and average annual unavailability or outage (U). These three basic reliability parameters can be calculated the following equations [3].
[image: image1.wmf] 

N

1

i

i

λ

s

λ

å

=

=

interruption/year

    (1)


[image: image2.wmf]hr/yr

 

N

1

i

i

r

i

λ

s

U

å

=

=




     (2)


 [image: image3.wmf]hr

   

s

r

s

U

s

r

=





     (3)

There are many outage types in distribution system. Among them these outage types such as permanent outages, temporary outages, transient outages, scheduled maintenance outages and utility outage are always happening in distribution system. According to the collecting data of distribution system, Kyaukse feeder is more interrupt than other feeders. Therefore, Kyaukse feeder need to improve the reliability for their customers. Furthermore, Fig. 1 shows the flow chart for calculation of reliability indices.

The basic indices are fundamentally important but they do not give the complete system behavior and response. Therefore, in this paper, the following reliability indices such as system average interruption frequency index (SAFI), system average interruption duration index (SAIDI), customer average interruption duration index (CAIDI), expected energy not supplied index (EENS), expected interruption cost index (ECOST), average energy not supplied index (AENS) and interrupted energy assessment rate index (IEAR) are calculated to get the complete assessment of distribution system. These equations are expressed as the following [4]. 

[image: image4.wmf]served

customer 

 

of

number 

 

total

ons

interrupti

customer 

 

of

number 

 

total

SAIFI

=



[image: image5.emf]Start

Select network 

component 

Calculate contribution to 

reliability indices 

Accumulate indices 

to affected load 

More components

Result presentation

Stop

Yes

No


Fig. 1. Flow Chart for Calculation of Reliability Indices

[image: image6.wmf]i

N

i

N

i

λ

å

å

=

failure/customer/year
       
      (4)
[image: image7.wmf]served

customer 

 

of

number 

 

total

duration

on 

interrupti

customer 

 

of

 

sum

SAIDI

=



        



  [image: image8.wmf]i

N

i

N

i

U

å

å

=

hr/customer/year
 
      (5)
[image: image9.wmf]ons

interrupti

customer 

 

of

number 

 

total

duration

on 

interrupti

customer  

 

of

 

sum

CAIDI

=




 


 [image: image10.wmf]i

N

i

λ

i

N

i

U

å

å

=

hr/customer interruption/year
      (6)
[image: image11.wmf]demanded

 

hours

customer 

service

 

available

 

of

 

hours

customer 

ASAI

=


 

      




  
 [image: image12.wmf]8760

*

i

N

i

N

i

U

8760

*

i

N

å

å

-

å

=

  

     (7)
ASUI = 1- ASAI



     (8)

EENSi = Pi* Ui   MWh/year

      (9)


EENS = [image: image13.wmf]å

N

i

i

EENS

MWh/year

    (10)



ECOSTi = [image: image14.wmf]å

N

i

i

)

λ

i

f(r

i

P

  $/year

    (11)


ECOST = [image: image15.wmf]å

N

i

i

ECOST

MWh/year

    (12)

[image: image16.wmf]served

customer 

 

of

number 

 

total

system

  

by the

 

supplied

not 

energy 

 

total

AENS

=



   




     [image: image17.wmf]i

N

i

EENS

å

å

=





    (13)

  IEAR = [image: image18.wmf]i

EENS

i

ECOST



                       (14)


Where Pi is average load demand and Ui is outage time at load point i, ASAI is average service availability index, ECOST is expected interruption cost index, IEAR is interrupted energy assessment rate index and ASUI is average service unavailability index [5].

III. Using the Template

This paper presents 33/11 kV Kyaukse Feeder line of Kyatminton substation as case study and the ETAP software was used to analyze the reliability assessment of test system. This paper also analyzed the reliability improvement by integrating the distributed energy resource (DER) to the distribution network of 33/11 kV Kyaukse Feeder of Kyaukse (Kyatminton) Substation. Fig.2 shows the one-line diagram of the test system from Kyaukse Feeder. The customer types of test system are presented in Table I.

[image: image19.emf]33 

kV 

11 kV

LP 1

LP 2

LP 3

LP 14

LP 15

LP 16

LP 

23

LP 28

LP 29

LP 32

LP 34

LP 39

LP 

4

LP 

5

LP 10

LP 13

LP 12

LP 11

LP 9

LP 8

LP7

LP 

6

LP 18

LP 

20

LP 

19

LP 

22

LP 

21

LP 24

LP 25

LP 26

LP 27

LP 30

LP 31

LP 33

LP 38

LP 35

LP 36

LP 37

LP 40

Kyaukse

LP 17


Fig. 2. One Line Diagram of Test System

TABLE I. Input Data for Reliability Assessment of Test System
	Load Point
	Customer Type
	Average Load per Load Point(kW)


	No. of Customer

	29
	G & I
	22.1
	1

	14,18,33,34,36,38
	Residential
	22.1
	317

	3,9,12,13,17,24,
	Commercial
	22.1
	6

	11,20,25,26,32,37,39,40
	Residential
	32.3
	828

	15,30
	Commercial
	32.3
	2

	10,6,27,35
	Residential
	41.65
	567

	7,8
	Commercial
	41.65
	2

	19,21,28,31,
	Residential
	51.85
	734

	1
	G&I
	62.05
	1

	22
	G&I
	72.25
	1

	5
	Commercial
	121
	1

	2
	G&I
	132
	220

	16
	Residential
	142
	366

	4
	Residential
	192
	369

	23
	Residential
	262
	183

	Total
	3598


There are forty load points and its length has 8.5 miles and its lateral points have 0.5 miles. Its total load is 2 MW, total customer of kyaukse feeder is 3598. The basic indices such as average interruption rate (f/yr), average outage duration (hr) and annual outage duration (hr) are important to run the reliability assessment of test system. Fig. 3 shows the reliability assessment of test system before integrating DG in ETAP software.  
[image: image20.png]e e g0t
gt R R e
LAz
e
[ o "
v T30 26 2. 9 6 he
B S et
5 wh 20 = o
PR ke = v o
R S Sl o
e e Lulpin Lulpal e
|t SR g, SRR
e gyt R
el
o
i




Fig. 3. Reliability Assessment of Test System before Integrating DG by using ETAP Software
[image: image21.png]614
6135

i m
60.9 ||

1357 9111315171921232527293133353739
Load Point

Iy
2o
252
B

Failurefyear
I
202,

5202

280

3
b4




Fig. 4. Different Failures Rate of Each Load Points 

[image: image22.emf]0

10

20

30

40

50

60

70

80

90

0 10 20 30 40

EENS (MWh/yr)

Load Point


Fig. 5. Expected Energy Not Supply (EENS) of Forty Load Points in Test System


Fig.4 shows the different failures rate of each load points of test system. Moreover, the expected energy not supply (EENS) of each load point can been seen in Fig. 5 According to reliability assessment of test system by using ETAP Software, Average service Availability Index (ASAI) is 0.9642 pu, Expected Energy Not Supplied (EENS) is 643.359 MWh / year and Average Energy Not Supplied (AENS) is 0.1859 MWh/ customer/yr.
IV. Integrating the PV-Diesel Hybrid System 
When the reliability assesses the proposed system in the load shed and no load shed condition, the expected energy not supply is 643.36 MW hr/year and system availability has 96%. Therefore, the system need to be improve the reliability, decrease the energy not supply and increase the system availability. There are many ways to increase the system reliability: Reconfiguration, Capacitors Installation, Demand Side Management, Distribution Transformer Load Management and integrating the distributed generation 12]. In this paper, integrating PV-Diesel Hybrid System distributed generation is considered for reliability improvement of test system. Firstly, if the Hybrid system integrates as the distributed generation in the test system, the system is required to optimal location and size of distributed generation for reliability improvement [13].
In this paper, the method is considered for determining the placement for distributed generation (DG) in distribution system based on the system energy not supply and load flow analysis by using Newton Raphson Method. The proposed methodology aims to optimize the better location to reduce the power losses and improves the voltage profile and to optimize the distribution system in ETAP software.
[image: image23.png]0 5 10 15 20 25 30 35 40 45 50 55 60 65 70 75 80 85
Bus Number




Fig. 6. Choosing the location of Distributed Generation based on EENS

[image: image24.png]0.98
0.975
0.97
0.965
0.96
0.955
0.95
0.945
0.94

Voltage (p-u)

0 5 10 1520 25 30 35 40 45 50 55 60 65 70 75 80 85
Bus Number




Fig. 7. Choosing the Location of PV-Diesel Hybrid System based on the Voltage Drop
In choosing the location of distributed generation in proposed system, it can be considered in two conditions such as system expected energy not supply (EENS) in each bus when the system run in reliability assessment and real power losses in each bus when the system run in load flow analysis. It’s mention the choosing of DG location above two methods (EENS assessment and load flow analysis) and these results are shown in Fig.  6 and Fig. 7. According to the analysis, Bus 77 is optimal location to integrate the distributed generation in the distribution system.

For choosing the penetration level of distributed generation, the amount of DG must be put into relation to an area, e.g. local distribution system or nation-wide power network. The high penetration of DG is defined as DG penetration is obtained when DG is implemented to cover a 50% of load increment.
The penetration level (PL) can be defined as the following equation.


 
[image: image25.wmf]100%

P

P

P

PL

DGi

load

DGi

´

+

=



( 15)

where, PDGi stand for the total active power of all DG units installed in a given area and PLoad is the total active power of the load in the same area. In this paper, the penetration level of distributed generation is considered as 20%, 50%,70% of maximum load. 
In according with the load flow analysis of proposed system, 20% DG the penetration level is a point to integrate the optimal sizing in the distribution system. It’ level can be reduced the power losses, increase the voltage profile and improve the system reliability. This result is shown in Fig. 8. According to the analysis of optimal sizing for distributed generation, 300 kW PV and 200 kVA are connected as the hybrid system for reliability improvement.
[image: image26.png]Real Power Loss (MW)

o o © o o o
[ RO Y

0

0%

10% 20% 30% 40% 50% 60% 70% 80% 90% 100%
DG Penetration Level




Fig. 8. Choosing the size of Distributed Generation based on Load Flow Analysis
[image: image27.png]o0 9% 125 e -
308 x-S =
25T 100 1 T30 26 23" 26 g om0 30 Kins 990 K
> sig v e
T2 33 35 T30
315w P 50 xva 200 xvn 315w
B PP B S e e
BaE fs ne
R
@
27 T3
aas Lze LT Juo a1 -
2 ] . 200w
= e e 111‘ o019 2007 ) om0 E
o 259 225957 o3P s o Eadbd 315 pgpen®
36 b
s Lump3z
Lumpzs Lumpos Lump2e Lump27 Lm0 Lompay LTSS a1 50 ne
s 48 A 55 T 33 WA a5 e 38 KVA 61 kUA ES
el
s 635 mee.3s ne 639 br

3.12 b
872410 £/yx




Fig. 9. Reliability Assessment After Integrating PV-Diesel Hybrid System at Bus 77 in ETAP Software

[image: image28.png]700
600
500

300
200
100

EENS (MWhyr)
8

Expected Energy not Supply

= without DG

®with DG




Fig. 10. Comparison of Expected Energy Not Supply in Two Conditions

In this hybrid system, PV DG is usually operating as the grid connected type and diesel generator can only operate when the system has interruption occurs due to the various effects of faults. When the PV-Diesel hybrid system is integrated as the distributed generation at bus 77 with 20% of maximum load in test system as shown in Fig. 9, the system reliability is improved 27% based on the energy not supply (EENS). Moreover, comparison of expected energy not supply (EENS) and comparison of System Available Index (ASAI) in two conditions are respectively shown in Fig.10 and Fig. 11. Finally, the summary of reliability indices in two condition is shown in Table II.

[image: image29.png]ASAL (pu)

System Availability Index

0.975
0.97
0.965
0.96
0.955

mwithout DG mwith DG




Fig. 11. Comparison of System Availability Index in Two Conditions

TABLE II. Results of Reliability Analysis in Two Conditions

	Summary of Reliability Indices in Two Condition

	Indices
	Without DG
	With PV-Diesel Hybrid

	SAIFI
	61.1951 failures / customer.yr
	35.9855 failures / customer.yr

	SAIDI
	314 hr / customer.yr
	231.7  hr / customer.yr

	CAIDI
	5.131 hr / customer interruption
	6.4 hr / customer interruption

	ASAI
	0.9642 pu
	0.9735 pu

	ASUI
	0.03585 pu
	0.02645 pu

	EENS
	643.36 MW hr / yr
	470 MW hr / yr

	ECOST
	2,421,614.0 $/year
	1,885,166.0 $/year

	AENS
	0.1859 MW hr / customer.yr
	0.1358 MW hr / customer.yr

	IEAR
	3.764 $/kWh
	4 $/kWh


V. Conclusion

This paper investigates the effectiveness of improving the reliability of power distribution network with PV-Diesel Hybrid System of distributed generation (DG). ETAP software was used to determine the reliability analysis of test system. Comparison of reliability indices in normal case and PV-Diesel hybrid system of DG are respectively showed with result tables. According to the simulating results, the failure rate is decreased from 61.1951 to 35.9855 failure/customer.yr and expected energy not supply is decreased from 643.36 MW hr/yr to 470 MW hr/yr by integrating DG in test system. An important study is the behavior of distributed energy sources which allows employing the size and variable in time energy sources while providing a continuous supply.
Acknowledgment
The author would like to express her deepest appreciation to Yangon Technological University (YTU) for its support and then also thanks to Kyaukse Substation’s incharge for helping to get data. Especially, the author wish to express her sincere thanks to her teachers for ideas, sharing knowledge and their valuable times whenever the author want to discuss about her research. 
References
[1] Richard E. Brown. Electric Power Distribution Reliability (Second Edition), 2009 New York: Taylor & Francis Group.

[2] Roy Billinton, Ajit Kumar Verma, Rajesh Karki: Reliable and Sustainable Electric Power and Energy Systems Management. 

[3] Roy Billinton, Wenyuan Li: Reliability Assessment of Electric Power Systems Using Monte Carlo Methods

[4] R. Billinton and R. N. Allan, Reliability Evaluation of Power Systems, Plenum, New York, 1984.


[5] Ali A. Chowdhury, Don O. Koval: Power Distribution System Reliability Practical Methods and Applications. [2009]


[6] Satish Jonnavithula,”Cost/Benefit Assessment of  Power System Reiability”,   Department of Electrical Engineering, University of Saskarchewan,1997

[7] T.A.SHORT,”Electric Power Distributon Handbook” , ©2004by CRC Press  LLC

[8] Irfan Waseem, “Impacts of Distributed Generation on the Residential Distribution Network Operation” January 2008

[9] Jin Woo Jung. 2005.“Modeling and Control of Fuel Cell Based Distributed Generation System”, Ph.D. Dissertation, University of Ohio State.  Columbus,USA.

[10] T. Q. D. Khoa, P. tt Binh et al., “Optimizing location and sizing of distributed generation in distribution systems,” in 2006 IEEE PES Power Systems Conference and Exposition. IEEE, 2006, pp. 725–732.

[11]  P. Dondi, D. Bayoumi, C. Haederli, D. Julian, and M. Suter, “Network integration of distributed power generation,” Journal of power sources, vol. 106, no. 1, pp. 1–9, 2002.

[12] T. Dorji, “Reliability assessment of distribution systems,” Master of Science in Electric Power Engineering, Norwegian University of Science and Technology, 2009.

[13] M. Al-Muhaini and G. T. Heydt, “Evaluating future power distribution system reliability including distributed generation,” IEEE Transactions on Power Delivery, vol. 28, no. 4, pp. 2264–2272, 2013.

[14] Angelopoulos, K. Integration of Distributed Generation in Low Voltage Networks, Power Quality and Economics. University of Strathclyde in Glasgow; 2004

XXX-X-XXXX-XXXX-X/XX/$XX.00 ©20XX IEEE


_1630864438.xls
Chart1

		19.40241

		41.21518

		6.916545

		60.15367

		37.81615

		22.64879

		13.05636

		13.06347

		6.935403

		13.07768

		10.14185

		6.942946

		6.946763

		6.9196

		10.11927

		44.4717

		6.925709

		6.932536

		16.27198

		10.1399

		16.28253

		13.08372

		82.11527

		6.934874

		10.14003

		10.14449

		13.08685

		16.57508

		9.891644

		10.15789

		16.3133

		6.956257

		6.959312

		6.962367

		13.14001

		6.975303

		10.19918

		6.969194

		10.18468

		10.18921



Load Point

EENS (MWh/yr)



Sheet1

		

										without Load Shed												with DG																with Load Shed

										λ		r		U		EENS								λ		r		U		EENS								λ		r		U		EENS

								1		55.07		5.46		300.69		18.66						1		35.98		6.39		230.08		14.28						1		61.0687		5.120283		312.689		19.40241

								2		55.08		5.46		300.83		39.63						2		35.98		6.39		230.08		30.31						2		61.08173		5.121453		312.8272		41.21518

								3		55.09		5.46		300.97		6.65						3		35.98		6.39		230.08		5.08						3		61.09478		5.122622		312.9655		6.916545

								4		55.11		5.46		301.14		57.85						4		36.00		6.56		236.12		45.36						4		61.11088		5.124065		313.1361		60.15367

								5		55.13		5.47		301.31		36.37						5		36.01		6.56		236.29		28.52						5		61.12698		5.125507		313.3068		37.81615

								6		55.14		5.47		301.48		21.78						6		36.03		6.56		236.47		17.08						6		61.14308		5.126948		313.4774		22.64879

								7		55.14		5.47		301.48		12.56						7		36.03		6.56		236.47		9.85						7		61.14308		5.126948		313.4774		13.05636

								8		55.16		5.47		301.65		12.56						8		36.04		6.57		236.64		9.86						8		61.15918		5.128389		313.6481		13.06347

								9		55.18		5.47		301.82		6.67						9		36.06		6.57		236.81		5.23						9		61.17529		5.129828		313.8187		6.935403

								10		55.19		5.47		301.99		12.58						10		36.08		6.57		236.98		9.87						10		61.19139		5.131268		313.9894		13.07768

								11		55.19		5.47		301.99		9.75						11		36.08		6.57		236.98		7.65						11		61.19139		5.131268		313.9894		10.14185

								12		55.21		5.47		302.16		6.68						12		36.09		6.57		237.15		5.24						12		61.20749		5.132706		314.16		6.942946

								13		55.22		5.47		302.33		6.68						13		36.11		6.57		237.32		5.24						13		61.22459		5.134092		314.3327		6.946763

								14		55.11		5.46		301.10		6.65						14		35.98		6.39		230.08		5.08						14		61.10781		5.123791		313.1037		6.9196

								15		55.14		5.46		301.29		9.73						15		36.00		6.39		230.13		7.43						15		61.13696		5.124399		313.2902		10.11927

								16		55.14		5.46		301.29		42.77						16		36.00		6.39		230.13		32.67						16		61.13696		5.124399		313.2902		44.4717

								17		55.13		5.47		301.38		6.66						17		35.98		6.39		230.08		5.08						17		61.1339		5.126127		313.3801		6.925709

								18		55.16		5.47		301.69		6.67						18		36.00		6.49		233.75		5.17						18		61.16304		5.128735		313.689		6.932536

								19		55.18		5.47		301.83		15.65						19		36.01		6.50		233.89		12.13						19		61.17608		5.129901		313.8272		16.27198

								20		55.19		5.47		301.93		9.75						20		36.02		6.50		233.99		7.56						20		61.18568		5.130759		313.929		10.1399

								21		55.20		5.47		302.03		15.66						21		36.03		6.50		234.09		12.14						21		61.19528		5.131617		314.0307		16.28253

								22		55.21		5.47		302.13		12.58						22		36.04		6.50		234.20		9.75						22		61.20588		5.132423		314.1345		13.08372

								23		55.16		5.47		301.66		78.97						23		35.98		6.39		230.08		60.23						23		61.15998		5.128461		313.6566		82.11527

								24		55.17		5.47		301.79		6.67						24		35.98		6.39		230.08		5.08						24		61.17302		5.129627		313.7948		6.934874

								25		55.19		5.47		301.93		9.75						25		35.98		6.39		230.08		7.43						25		61.18606		5.130793		313.933		10.14003

								26		55.20		5.47		302.07		9.76						26		35.98		6.39		230.08		7.43						26		61.1991		5.131958		314.0712		10.14449

								27		55.21		5.47		302.21		12.59						27		35.98		6.39		230.08		9.58						27		61.21214		5.133123		314.2094		13.08685

								28		55.24		5.48		302.52		15.94						28		36.00		6.40		230.25		12.13						28		61.24128		5.135724		314.5183		16.57508

								29		55.24		5.48		302.52		9.51						29		36.00		6.40		230.25		7.24						29		61.24128		5.135724		314.5183		9.891644

								30		55.24		5.48		302.49		9.77						30		35.98		6.39		230.08		7.43						30		61.23822		5.135452		314.4859		10.15789

								31		55.25		5.48		302.62		15.69						31		35.98		6.39		230.08		11.93						31		61.25126		5.136615		314.6241		16.3133

								32		55.26		5.48		302.76		6.69						32		35.98		6.39		230.08		5.08						32		61.26429		5.137778		314.7623		6.956257

								33		55.28		5.48		302.90		6.69						33		35.98		6.39		230.08		5.08						33		61.27733		5.138941		314.9006		6.959312

								34		55.29		5.48		303.04		6.70						34		35.98		6.39		230.08		5.08						34		61.29037		5.140102		315.0388		6.962367

								35		55.33		5.48		303.49		12.64						35		35.98		6.39		230.08		9.58						35		61.33255		5.143857		315.4859		13.14001

								36		55.35		5.49		303.62		6.71						36		35.98		6.39		230.08		5.08						36		61.34559		5.145017		315.6241		6.975303

								37		55.36		5.49		303.76		9.81						37		5.24		4.12		21.59		0.70						37		61.35963		5.146125		315.7643		10.19918

								38		55.32		5.48		303.35		6.70						38		35.98		6.39		230.08		5.08						38		61.31951		5.142697		315.3477		6.969194

								39		55.32		5.48		303.32		9.80						39		35.99		6.53		234.97		7.59						39		61.31645		5.142425		315.3152		10.18468

								40		55.33		5.48		303.46		9.80						40		36.01		6.53		235.12		7.59						40		61.33049		5.143535		315.4555		10.18921





Sheet1

		



Load Point

EENS (MWh/yr)




_1630866256.xls
Chart1

		EENS (MWh/yr)		EENS (MWh/yr)



without DG

with DG

EENS (MWh/yr)

Expected Energy not Supply

643.359

470



Sheet1

		

										320				320

								Year		Module Power (W)		PV Efficiency		Life Long		Pout		degradation								EENS (MWh/yr)								ASAI

								2018				14.5		100		320		1						Normal Case		643.359						Normal Case		0.9642

								2019				15		99				0.95						Type 1		570.351						Type 1		0.9678

								2020				15.5		98				0.9						Type 2		470						Type 2		0.9735

								2021				16		97				0.85						Type 3		495.305						Type 3		0.9721

								2022				16.5		96				0.8

								2023				17		95				0.75

								2024				17.5		94				0.7

								2025				18		93				0.65

								2026				18.5		92				0.6								EENS (MWh/yr)

								2027				19		91				0.55						Normal Case		643.359

								2028		320		19.5		90				0.5						Type 2		470

																						Year		Type 1		Type 2		Type 3

																				0.357		2018		$   0.146		$   0.159		$   0.255

																						2019		0.144		0.157		0.252

																						2020		0.143		0.156		0.249

																						2021		0.141		0.155		0.247

																						2022		0.14		0.153		0.245

																						2023		0.139		0.152		0.243

																						2024		0.138		0.151		0.242

																						2025		0.137		0.15		0.24

																						2026

																						2027

																						2028

						Year		Type 3														2029

						2018		$   0.255														2030

						2019		0.252														2031

						2020		0.249														2032

						2021		0.247														2033

						2022		0.245														2034

						2023		0.243														2035

						2024		0.242														2036

						2025		0.24														2037

																						2038

																						2039

																						2040

																						2041

																						2042

																						2043

																						2044





Sheet1

		



Type 1

Year

$/kWh



Sheet2

		



Type 1

Type 2

Type 3



		



Type 3



		



Normal Case

Type 1

Type 2

Type 3

EENS (MWh/yr)



		



Normal Case

Type 1

Type 2

Type 3

ASAI (p.u)

System Available Index



		



Normal Case

Type 2

EENS (MWh/yr)

Expected Energy not Supply



		

				T		It		Mt		Ot		Ft		r		St		d		=

				25		165530		1		15		7%		6%		1095000		0.50%

												10533		9028

										2019		2020		2021		2022		2023		2024		2025

						Installed Cost				$131,520		$117,272		$103,024		$88,776		$74,528		$60,280		$46,032				65%

						Annual Degradation				1%		0.95%		0.90%		0.85%		0.80%		0.75%		75.00%				25%

						Inverter Cost				$500		$450		$402		$354		$306		$258		$210				58%

						O & M expenses				15		13.975		12.95		11.925		10.9		9.875		8.85				41%

						Inverter Lifetime				10		10		11		14		15		15		15

						Module Efficiency				90%		90%		90%		90%		90%		90%		90%

						System Life				25		25		25		25		25		25		25

						Interest rate																				13%

						Discount rate






_1630866373.xls
Chart1

		ASAI		ASAI



without DG

with DG

ASAI (p.u)

System Availability Index

0.9642

0.9735



Sheet1

		

										320				320

								Year		Module Power (W)		PV Efficiency		Life Long		Pout		degradation								EENS (MWh/yr)								ASAI								ASAI

								2018				14.5		100		320		1						Normal Case		643.359						Normal Case		0.9642						without DG		0.9642

								2019				15		99				0.95						Type 1		570.351						Type 1		0.9678						with DG		0.9735

								2020				15.5		98				0.9						Type 2		470						Type 2		0.9735

								2021				16		97				0.85						Type 3		495.305						Type 3		0.9721

								2022				16.5		96				0.8

								2023				17		95				0.75

								2024				17.5		94				0.7

								2025				18		93				0.65

								2026				18.5		92				0.6								EENS (MWh/yr)

								2027				19		91				0.55						Normal Case		643.359

								2028		320		19.5		90				0.5						Type 2		470

																						Year		Type 1		Type 2		Type 3

																				0.357		2018		$   0.146		$   0.255		$   0.159

																						2019		0.144		0.252		0.157

																						2020		0.143		0.249		0.156

																						2021		0.141		0.247		0.155

																						2022		0.14		0.245		0.153

																						2023		0.139		0.243		0.152

																						2024		0.138		0.242		0.151

																						2025		0.137		0.24		0.15

																						2026

																						2027												PV		PV-Diesel		Diesel

																						2028												$0.14		$0.15		$0.24

						Year		Type 3														2029

						2018		$   0.255														2030

						2019		0.252														2031

						2020		0.249														2032

						2021		0.247														2033

						2022		0.245														2034

						2023		0.243														2035

						2024		0.242														2036

						2025		0.24														2037

																						2038

																						2039

																						2040

																						2041

																						2042

																						2043

																						2044





Sheet1

		



Type 1

Year

$/kWh



Sheet2

		



Type 3



		



Normal Case

Type 1

Type 2

Type 3

EENS (MWh/yr)



		



Normal Case

Type 1

Type 2

Type 3

ASAI (p.u)

System Available Index



		



Normal Case

Type 2

EENS (MWh/yr)

Expected Energy not Supply



		





		



without DG

with DG

ASAI (p.u)

System Availability Index



		

				T		It		Mt		Ot		Ft		r		St		d		=

				25		165530		1		15		7%		6%		1095000		0.50%

												10533		9028

										2019		2020		2021		2022		2023		2024		2025

						Installed Cost				$131,520		$117,272		$103,024		$88,776		$74,528		$60,280		$46,032				65%

						Annual Degradation				1%		0.95%		0.90%		0.85%		0.80%		0.75%		75.00%				25%

						Inverter Cost				$500		$450		$402		$354		$306		$258		$210				58%

						O & M expenses				15		13.975		12.95		11.925		10.9		9.875		8.85				41%

						Inverter Lifetime				10		10		11		14		15		15		15

						Module Efficiency				90%		90%		90%		90%		90%		90%		90%

						System Life				25		25		25		25		25		25		25

						Interest rate																				13%

						Discount rate













































33 kV
11 kV
LP 1
LP 2
LP 3
LP 14
LP 15
LP 16
LP 23
LP 28
LP 29
LP 32
LP 34
LP 39
LP 4
LP 5
LP 10
LP 13
LP 12
LP 11
LP 9
LP 8
LP7
LP 6
LP 18
LP 20
LP 19
LP 22
LP 21
LP 24
LP 25
LP 26
LP 27
LP 30
LP 31
LP 33
LP 38
LP 35
LP 36
LP 37
LP 40
Kyaukse


LP 17



